## Sheet1
Input |  |  |  | comment
all wires in series for cooling
Tube Outer Diameter | D | 2.54 | mm
Tube Inner diameter | d | 1.54 | mm
Tube Length (total) | l | 6 | m | 6 wires * 1meter assumed in series for cooling ONLY
Tube electric length |  | 2 | m | 2 wires * 1meter are actually fed
Cu Resisivity | ρ | 1.7e-08 | Ω.m
Applied Current | I | 300 | A
Temperature Rise | ΔT | 52 | K | i.e. 80 degrees max; might be too high; ask Gerard
Specific heat H2O | c | 4180 | J/kg.K
Calculations
Cu Surface | A | 3.2044e-06 | m2
Cu Resistance | R | 0.01061 | Ω
Dissipated Power | P | 954.9297 | W
Water Flow | m | 0.0043933 | kg/s
|  | 0.26307 | l/min | ask Gerard for l/min minimum for interlock
Pressure drop | Δp | 4.399 | bar | dp min is 4.5 bar